## README
Read me
Drawing SYN-HARD-019 (synthetic). Draft generated from the P&ID only.
HAZOP_draft: starting point for a HAZOP team. Causes, consequences and safeguards must be challenged;
severity, likelihood and recommendations are the team's decision.
Safeguards listed are only those found on this drawing, each with its tag.
Review_flags: anything the reader was unsure about. Check these on the drawing first.

## HAZOP_draft
node | equipment | parameter | guideword | deviation | causes | consequences | safeguards_on_drawing | gap_for_team_review
N01 T-601 (tank) | T-601 | Level | More | High level | LV-611 fails closed / LIC mis-set; downstream P-602A stopped | tank overfill, loss of containment | LAH-611 (high-level alarm, operator response) | No independent high-high level trip found on drawing; team to decide if one is needed (LOPA).
N01 T-601 (tank) | T-601 | Level | Less | Low level | LV-611 fails open | loss of suction to P-602A: cavitation, seal damage; gas blow-by through LV-611 to P-602A | LAL-611 (low-level alarm, operator response)
N01 T-601 (tank) | T-601 | Pressure | More | High pressure | outlet blocked (LV-611 closed); external fire | overpressure, possible loss of containment | PAH-613 (high-pressure alarm); PSV-615 (relief valve)
N01 T-601 (tank) | T-601 | Temperature | More | High temperature | high feed temperature | vapour generation, pressure rise | TT-614 (indication only) | No high-temperature alarm found; temperature indication only or none.
N02 P-602A (pump) incl. inlet 8"-P-6001 | P-602A | Flow | No | No / low flow | low level in T-601; pump trip (power, mechanical) | pump runs dry or deadheaded: overheating, seal failure; loss of feed to E-603 | LAL-611 (low level on suction vessel T-601)
N02 P-602A (pump) incl. inlet 8"-P-6001 | P-602A | Flow | Reverse | Reverse flow | pump stops while discharge side is at higher pressure | backflow into T-601; reverse rotation | NRV-612 (check valve)
N02 P-602A (pump) incl. inlet 8"-P-6001 | P-602A | Pressure | More | High discharge pressure | discharge blocked downstream | pump deadheaded; downstream overpressure if shut-off exceeds design | none found on drawing | Confirm pump shut-off pressure against downstream design pressure.
N03 E-603 (heat exchanger) incl. inlet 4"-P-6002 | E-603 | Temperature | More | High outlet temperature | loss of cooling / heating medium upset; tube fouling | high temperature to V-604 | none found on drawing | No high-temperature alarm on the outlet found on drawing.
N03 E-603 (heat exchanger) incl. inlet 4"-P-6002 | E-603 | Flow | Less | Low / no process flow | upstream P-602A stops | overheating of process side, thermal stress | none found on drawing | Team to confirm protection (not identifiable from this drawing).
N03 E-603 (heat exchanger) incl. inlet 4"-P-6002 | E-603 | Composition | Other than | Tube leak | tube failure / corrosion | cross-contamination between process and utility | none found on drawing | Not detectable from this drawing; confirm leak detection philosophy.
N04 V-604 (drum) incl. inlet 4"-P-6003 | V-604 | Level | More | High level | inflow from E-603 above outlet capacity | liquid carry-over to downstream | LAH-616 (high-level alarm, operator response) | No independent high-high level trip found on drawing; team to decide if one is needed (LOPA).
N04 V-604 (drum) incl. inlet 4"-P-6003 | V-604 | Level | Less | Low level | loss of feed from E-603 | level lost, downstream starved | none found on drawing
N04 V-604 (drum) incl. inlet 4"-P-6003 | V-604 | Pressure | More | High pressure | external fire | overpressure, possible loss of containment | PAH-618 (high-pressure alarm); PSV-619 (relief valve)
N04 V-604 (drum) incl. inlet 4"-P-6003 | V-604 | Temperature | More | High temperature | loss of cooling in E-603 | vapour generation, pressure rise | none found on drawing | No high-temperature alarm found; temperature indication only or none.

## Drawing_register
item | kind | detail | found_by
T-601 | equipment | tank | tag inside outline
P-602A | equipment | pump | tag inside outline
E-603 | equipment | heat exchanger | tag inside outline
V-604 | equipment | drum | tag inside outline
8"-P-6001 | process line | T-601 -> P-602A; valves: LV-611 | thick polyline + arrowhead
4"-P-6002 | process line | P-602A -> E-603; valves: NRV-612 | thick polyline + arrowhead
4"-P-6003 | process line | E-603 -> V-604; valves: - | thick polyline + arrowhead
PSV-615 | relief valve | on T-601 | nearest equipment
PSV-619 | relief valve | on V-604 | nearest equipment
LAL-611 | instrument | on T-601 | signal line
LAH-616 | instrument | on V-604 | signal line
LT-611 | instrument | on T-601 | same loop
LIC-611 | instrument | on T-601 | same loop
LAH-611 | instrument | on T-601 | same loop
PT-613 | instrument | on T-601 | proximity
PAH-613 | instrument | on T-601 | proximity
TT-614 | instrument | on T-601 | proximity
LT-616 | instrument | on V-604 | same loop
LIC-616 | instrument | on V-604 | same loop
PT-618 | instrument | on V-604 | proximity
PAH-618 | instrument | on V-604 | proximity

## Review_flags
flag
line 8"-P-6001: no arrowhead, flow direction assumed left to right
line 4"-P-6002: no arrowhead, flow direction assumed left to right
overlapping bubbles near (869, 301): text 616 could not be paired - check by eye
overlapping bubbles near (885, 301): text 617 could not be paired - check by eye
instrument PT-613: no signal line, attached to nearest item T-601 (65 pt)
instrument PAH-613: no signal line, attached to nearest item T-601 (65 pt)
instrument TT-614: no signal line, attached to nearest item T-601 (94 pt)
instrument PT-618: no signal line, attached to nearest item V-604 (65 pt)
instrument PAH-618: no signal line, attached to nearest item V-604 (94 pt)